Ref No: GEEC / SAT/C2/Q4/STP/___/___              Date: __/__/____

To,

M/s.

Kind Attn: Mr

Sub		: Quotation for Sewage Treatment Plant ( MBBR for 300 m3/day capacity )

Ref		: The discussion had with you.

Dear Sir,

With reference to the discussion had with you on the above subject matter, we are submitting you our offer for the sewage treatment plant followed by Ultra Filtration System. The UF system helps in reducing the bacterial count and also in BOD, COD level of the sewage water. The treated water can be used for flushing purpose ( without human touch) and for gardening purpose.

We are one of the up - growing & a leading organisation in the field of Environmental Pollution Prevention and Control & have already executed similar assignment in the past which even today after installation are giving excellent results to our client.

Please find enclosed herewith our complete offer.

If you require any further clarification on the above subject matter, fell free to contact us.

Awaiting for your positive reply at the earliest.

Thanking you in anticipation.

Yours Faithfully,

For GREENEARTH ENGINEERS & CONSULTANTS.

SATISH RAO.

SEWAGE TREATMENT PLANT

FOR

M/s ---------

---------

## PREPARED BY

## GREENEARTH ENGINEERS & CONSULTANTS

## 515, E Wing, Kailsah Ind Complex, Park Site, Vikhroli (W),

## Mumbai – 400 079

## Tel 022- 2518 2018/19

## Email: satishrao@greenearthcon.com

## www.greenearthcon.com

CONTENTS

| Annexure I | Basis Of Design. |
| --- | --- |
| Annexure II | Description of treatment scheme. |
| Annexure III | Dimensional details of civil units. |
| Annexure IV | List of Mechanical equipment’s, piping works & Instruments. |
| Annexure V | List of Makes. |
| Annexure VI | Schedule of Exclusion. |
| Annexure VII | Commercial Terms & Conditions |
| Annexure IX | Drawing. |

ANNEXURE - I

Design Calculation for generation of sewage quantity.

| 1. | Total No. of flats |  |
| --- | --- | --- |
| 2. | No of persons in each flats | 5 nos. |
| 3. | Therefore Total No. of person | --- x 5 = --- Nos. |
| 4. | Total No of shops | --- nos. |
| 5. | No of person in each Shop | 2 nos. |
| 6. | Therefore Total No. of person | --- nos. |
| 7. | Amount of water used by per person in each shop | 25 ltr/day |
| 8. | Amount of water used by per persons in each flat | 135 ltr./day |
| 9. | Therefore total water used in flats | 135 x ---- = ----------ltr/day |
| 10. | Therefore total water used in shops | 25 x --- = ---- |
| 11. | Consider 90 % of water will come out as waste water | -------- x 90 /100 = ---------ltr/day |
| 12. | Therefore the plant is deign for | 300 m3/day |

II. DETAILS OF RAW SEWAGE & TREATED SEWAGE QUALITY

| Sr. No. | Parameters | Value (mg/lt) |  |
| --- | --- | --- | --- |
|  |  | Before | After Treatment |
| 01 | pH | 6-8 | 6.5 - 9 |
| 02 | Total Suspended Solids | 150 - 200 | < 50 |
| 03 | Oil & Grease | 100 - 200 | < 10 |
| 04 | BOD @ 3 days 270C | 350-500 | <10 |
| 05 | COD | 600-800 | <50 |
| 06 | TDS | 500 - 600 | <400 |
| 07 | Total Nitrogen | 50-100 | <10 |
| 08 | Ammonical Nitrogen | 10-50 | <5 |
| 09 | Phosphates | 20-50 | <5 |
| 10 | Residual Chlorine | 5-10 | <1.0 |

All parameters except pH are expressed in mg/lt.

ANNEXURE - II

DESCRIPTION OF THE TREATMENT PLANT

The following treatment scheme is adopted based on the characteristics of the sewage.

Initially the sewage will be passed through the screen chamber to remove any floating objects. It will then be taken to the oil & grease chamber for the removal of any oil that might be present. After this the sewage will be collected in the Collection Tank from which it will be pumped to the Aeration Tank using the Sewage Transfer Pump. The Activated Sludge Process (ASP) that takes place here involves removal of suspended and dissolved organic matter from the wastewater which creates Biological Oxygen Demand. This reduces the Dissolved Oxygen (D.O.) which if not arrested would lead to septic condition and foul smell.

The Moving Bed Biological Reactor (MBBR) process combines the advantages of two fundamental biological treatment processes, namely fixed technology and suspended growth technology (conventional activated sludge), into one hybrid system.

By combining high biomass quantities typical of MBBR technologies with fluidization typical of a conventional activated sludge, the process achieves high removal rates in a small volume of effluent. The attached growth significantly increases the microbial population within the tank, thereby increasing the Sludge Retention Time (SRT) of the system without increasing the suspended growth population.

This system is based on retention of adequate biomass. Suspended growth systems are known as activated sludge. The basic system consists of an Aeration Tank and a Clarifier. Bacteria grow by consuming organic matter (Food) in the Aeration Tank. They are separated from the wastewater in the Clarifier and returned to the Aeration Tank for further growth normally termed as Mixed Liquor Suspended Solids (MLSS). MLSS in the range of 3500 - 4000 mg/lt, is considered suitable for the design of ASP. Food to Micro - Organism ratio (f/m)

in the range of 0.1 - 0.3 is considered best to design an Activated Sludge Process. The activated sludge is biologically active and it contains a great number of aerobic bacteria and other micro - organisms that have got an unusual capacity to oxidize organic matter.

Air is provided to supply oxygen to the bacteria; to keep the sludge in suspension and also to prevent foul smell in the effluent. Sludge recirculation pumps return the sludge by pumping it back to the Aeration Tank. The clear, treated sewage from the Clarifier will be taken to the Filter Feed Tank.

The Filter Feed Tank is provided with an air grid. The sewage from the Filter Feed Tank will be pumped into the Dual Media Filter with help of two centrifugal non clog, self priming pumps having a capacity of 13.6 m 3/ hr @ 30-35 m head.

The Dual Media Filter is made out of MS/FRP and contains sand media. Its function is to remove suspended and organic matter present in the sewage. The sewage is then passed through an Activated Carbon Filter. In this filter organic matter will be adsorbed on to the carbon layer. The treated water is then passed through the Ultrafiltration system. The UF system - as the name indicates - removes suspended solids, bacteria and pathogens from sewage. It works by taking into consideration the molecular weight of particles. It basically filters out the particles having higher molecular size & weight. The pore size of the UF membrane is around 0.04 µ. The UF system brings down the COD & BOD level as well as the bacterial count in the treated sewage. The UF system works using a PLC base panel and is fully automatic.  The clear sewage will then be collected in the Treated Water Tank and will now be used for gardening and flushing (it cannot be used for drinking or washing purposes). The STP is provided with a monitoring device to test the pH, BOD & TSS which gives continuous real time data of the treated sewage.

The excess sludge from the Secondary Clarifier will be taken to the Centrifuge.  Dried sludge shall be carted away for land filling. In addition to the processes mentioned above the sewage treatment plant will also include piping, electrical work and instrumentation. For further details refer Annexure III & IV.

ANNEXURE - III

DIMENSIONAL DETAILS OF CIVIL UNITS

1) Unit No. 1

| a) | Name of the unit | Screen Chamber |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 5 m3 |
| d) | MOC | RCC M 20 |

2) Unit No. 2

| a) | Name of the unit | Oil & Greases Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 11 m3 |
| d) | MOC | RCC M 20 |

3) Unit No. 3

| a) | Name of the unit | Collection Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 135 m3 |
| d) | MOC | RCC M 20 |

4) Unit No. 4

| a) | Name of the unit | Aeration Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 130 m3 |
| d) | MOC | RCC M 20 |

5) Unit No. 5

| a) | Name of the unit | Secondary Settling Tank/Secondary Clarifier |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 49 m3 |
| d) | MOC | RCC M 20 |

6) Unit No. 6

| a) | Name of the unit | Filter Feed Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 65 m3 |
| d) | MOC | RCC M 20 |

7) Unit No. 7

| a) | Name of the unit | Foundation for Blower, Pump, Filter & Filter Press |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | Suitable |
| d) | MOC | RCC M 15 |

8) Unit No. 8

| a) | Name of the unit | Treated Water Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity | 65 m3 |
| d) | MOC | RCC M 20 |

9) Unit No. 9

| a) | Name of the unit | Sludge Holding Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity |  |
| d) | MOC | RCC M 20 |

10) Unit No. 10

| a) | Name of the unit | MCC & Filter Room |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity |  |
| d) | MOC | Brick Masonry |

11) Unit No. 11

| a) | Name of the unit | Flushing Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity |  |
| d) | MOC | RCC M 20 |

12) Unit No. 12

| a) | Name of the unit | Garden Tank |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Size/ Capacity |  |
| d) | MOC | RCC M 20 |

ANNEXURE - IV

LIST OF MECHANCIAL EQUIPMENTS, PIPING

WORKS AND INSTRUMENTS.

1.  AIR BLOWER FOR AERATION TANK & COLLECTION TANK.

| a) | Type | Twin lobe positive displacement air blower |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Capacity | 375m3/hr @ 4500 mm wg |
| d) | MOC of Body, rotors, plates | C.I FG 260 IS 210 |
| e) | Blower Speed | 1350 rpm |
| f) | Noise level at 1.5 mtr distance | 89 db (A) |
| g) | Type of bearing/Make | Antifriction / SKF/FAG |

2.  MOTOR FOR AIR BLOWER

| a) | Type | TEFC Sq., cage Induction Motor, Suitable for 450 volts, 50 heads size, 3 phase A.C supply with IP 55 protection and Class ‘B’ Insulation suitable for 43 0 C ambient temperature. |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Motor Rating | 12.5 hp/1500 rpm |
| e) | MOC | C.I |

3.  AIR GRID IN THE COLLECTION TANK

| a) | Type | Perforated pipe/ Cores diffusers |
| --- | --- | --- |
| b) | Quantity | 1 lot. |
| c) | MOC | UPVC/ PVC |

4.  SEWAGE TRANSFER PUMP

| a) | Type | Horizontal centrifugal, Self-priming, non-clog |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Capacity | 13.6 m3/hr @ 10-12 m head |
| e) | MOC | C.I |

5.  MOTOR FOR SEWAGE TRANSFER PUMP

| a) | Type | TEFC Sq., cage Induction Motor, Suitable for 450 volts, 50 heads size, 3 phase A.C supply with IP 55 protection and Class ‘B’ Insulation suitable for 43 0 C ambient temperature. |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Motor Rating | 2 hp/ 3000 rpm |
| e) | MOC | C.I |

6.  RETURN SLUDGE PUMP

| a) | Type | Horizontal centrifugal, Self-priming, non-clog |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Capacity | 13.6 m3/hr @ 10-12 m head |
| e) | MOC | C.I |

7.  MOTOR FOR RETURN SLUDGE PUMP

| a) | Type | TEFC Sq., cage Induction Motor, Suitable for 450 volts, 50 heads size, 3 phase A.C supply with IP 55 protection and Class ‘B’ Insulation suitable for 43 0 C ambient temperature. |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Motor Rating | 2 hp/ 3000 rpm |
| e) | MOC | C.I |

8. FILTER FEED PUMP

| a) | Type | Horizontal centrifugal, Mon block |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Capacity | 13.6 m3/hr @ 30-35 m head |
| e) | MOC | C.I |

9. DUAL MEDIA FILTER

| a) | Type | Vertical, pressure vessel |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Media | Sand of different grades |
| d) | Size | 1.2 m dia x 1.5 m hos |
| e) | MOC | MS epoxy painted from inside/ FRP |
| f) | Valves | 5 nos Butterfly Valve / MPV |

10. ACTIVATED CARBON FILTER

| a) | Type | Vertical, pressure vessel |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Media | Sand media at bottom with carbon iodine no 900 at the top |
| d) | Size | 1.2 m dia x 1.5 m hos |
| e) | MOC | MS epoxy painted from inside/ FRP |
| f) | Valves | 5 nos Butterfly Valve / MPV |

11. AIR GRID IN THE AERATION TANK

| a) | Type | Diffuser Membrane. |
| --- | --- | --- |
| b) | Quantity | 1 lot. |
| c) | Flow rate per DM | 10 m3/hr / 5 m3/hr |
| d) | Size | 90 mm dia x 1.0 m lgth/ 63 mm dia x 0.5 m lgth |
| e) | MOC | EPDM |

12. SLUDGE TRANSFER PUMP

| a) | Type | Horizontal centrifugal, Self-priming, non-clog |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Capacity | 13.6 m3/hr @ 10-12 m head |
| e) | MOC | C.I |

13. MOTOR FOR SLUDGE TRANSFER PUMPS

| a) | Type | TEFC Sq., cage Induction Motor, Suitable for 450 volts, 50 heads size, 3 phase A.C supply with IP 55 protection and Class ‘B’ Insulation suitable for 43 0 C ambient temperature. |
| --- | --- | --- |
| b) | Quantity | 2 nos. |
| c) | Mounting | Foot Mounted |
| d) | Motor Rating | 2 hp/ 3000 rpm |
| e) | MOC | C.I |

14. INSTRUMENTATION

| a) | Pressure Gauge | 4 nos. |
| --- | --- | --- |
| b) | Flow Meter | 1 no. ( Mechanical Type) |
| c) | Level Sensor | 1 no. |

15. ELECTRICAL PANEL (Distribution Box)

| a) | Body Thickness | 14 SWG |
| --- | --- | --- |
| b) | Doors Thickness | 16 SWG |
| c) | Base Frame Size | 75 mm x 40 mm x 3 mm thk |
| d) | Construction | Single Front, Cubical fixed feeders |
| e) | Finish | Powder Coating |
| f) | Shade | Siemens Grey |
| g) | Internal Wiring | 660/1100 V, PVC insulated copper flexible |
| h) | PLC with HMI | 1 no for UF system |

16. FILTER PRESS

| a) | Type of element | PP Recesses Type |
| --- | --- | --- |
| b) | Type of Discharge | Open discharge |
| c) | Closing Mechanism | Rachet Type |
| d) | Drainage Surface | PIPPS |
| e) | Plate Size | 24” x 24” |
| f) | Cake Thickness | 25 mm |
| g) | Feed nozzle | mm |
| h) | No of chambers | 19 nos. |
| i) | Feed Head MOC | CI/MS |
| j) | Fixed End MOC | CI/MS |
| k) | Moving Plate MOC | CI/MS |
| l) | Roller MOC | CI/MS |
| m) | Plates MOC | PP |
| n) | Hydraulic type | Motorized/ Hand pump |
| o) | Quantity | 1 set |

17. BAR SCREEN

| a) | Type | Rake type Mechanism, Coarse screen |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Space between the bar | 10 -15 mm |
| d) | Size | Suitable to the screen chamber |
| e) | MOC | MS epoxy painted/ SS |

18. INTERCONNECTING PIPING & VALVES

| a) | Type | UPVC Pipe & PP valves |
| --- | --- | --- |
| b) | Quantity | 1 lot. |
| c) | Air line outside the tanks MOC | MS |
| d) | Quantity | 1 lot. |

19. HYPOCHLORITE DOSING TANK

| a) | Type | Vertical, cylindrical, open top |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 100 ltr |
| d) | MOC | HDPE |

20. HYPOCHLORITE DOSING PUMP

| a) | Type | Diaphragm type |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 0-12 lph |
| d) | MOC | PP |

21. ALUM DOSING TANK

| a) | Type | Vertical, cylindrical, open top |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 100 ltr |
| d) | MOC | HDPE |

22. ALUM DOSING PUMP

| a) | Type | Diaphragm type |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 0-12 lph |
| d) | MOC | PP |

23. TUBE MEDIA

| a) | Type | Hexagonal chevron shaped |
| --- | --- | --- |
| b) | Quantity | 1 lot. |
| c) | Height | 750 mm/500 mm |
| d) | MOC | PP |
| e) | Tube Fitting | Tongue and Groove |
| f) | Thickness | 1.1mm (+/- 0.1 Mm) |
| g) | Maximum Continuous Working Temperature | 550. C |
| h) | Colour | Black |

24. BIO PACK MEDIA (MBBR)

| a) | Type | Fluidized Random Bio Media |
| --- | --- | --- |
| b) | Quantity | 1 lot. |
| c) | Colour | Black |
| d) | Size | 22 mm dia x 16 mm ht |
| e) | MOC | PP / PVC |

25. ULTRAFILTRATION MEMBRANE

| a) | Type | Hollow Fiber Membrane |
| --- | --- | --- |
| b) | No of membrane | 4 Nos. |
| c) | Flow Type | Outside –In |
| d) | Permeate Flow | 13.6 m3/hr |
| e) | Membrane MOC | Hydrophilic (polyvinylidene difluoride) |
| f) | Membrane pore size | 0.04 µ |
| g) | Housing MOC | UPVC |
| h) | Module Mounting | Vertical |
| i) | Valves Types | Electrically actuated |
| j) | MOC of valves | SS 304 |
| k) | No of valves | 6 nos. |
| l) | Rota meter | 2 Nos. |
| m) | Molecular weight cut off | 1,50,000 |
| n) | Backwash duration | 120 sec |

26.  UF BACK WASH PUMP

| a) | Type | Horizontal centrifugal, Mon block |
| --- | --- | --- |
| b) | Quantity | 1 nos. |
| c) | Mounting | Foot Mounted |
| d) | Capacity | 13 m3/hr @ 20 m head |
| e) | MOC | SS |

27.  PERMEATE  CUM CIP TANK

| a) | Type | Vertical, Cylindrical |
| --- | --- | --- |
| b) | Quantity | 1 Nos. |
| c) | Color | Black |
| d) | Capacity | 5000 Ltr |
| e) | MOC | HDPE |

28. ACID DOSING TANK

| a) | Type | Vertical, cylindrical, open top |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 500 ltr |
| d) | MOC | HDPE |

29. ACID DOSING PUMP

| a) | Type | Diaphragm type |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 0-30 lph |
| d) | MOC | PP |

30. NAOCL DOSING TANK

| a) | Type | Vertical, cylindrical, open top |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 500 ltr |
| d) | MOC | HDPE |

31. NAOCL DOSING PUMP

| a) | Type | Diaphragm type |
| --- | --- | --- |
| b) | Quantity | 1 no. |
| c) | Capacity | 0-30 lph |
| d) | MOC | PP |

32. MICRON FILTRATION UNIT-5 MICRON

| a) | Type | Cartridge Filter |
| --- | --- | --- |
| b) | Quantity | 1 No. |
| c) | Flow Rate | 13.6 m3/hr |
| d) | Filtration Porosity | 5 Micron |
| e) | Filter MOC | Polypropylene |
| f) | Housing MOC | PP/SS 304 |
| g) | Length | 30” |
| h) | No of cartridge | 6 nos. |

33. Skid

| a) | MOC | MS powder coated |
| --- | --- | --- |
| b) | Size | Suitable |
| c) | Quantity | 1 No. |

ANNEXURE - V

LIST OF MAKES

| 1 | C.I Pumps | Kirloskar/Johnson/Eq. |
| --- | --- | --- |
| 2 | Dosing Pumps | E- Dose/Pratham/ Filtra/Eq. |
| 3 | Dosing Tanks | Sintex/ Infra /Eq. |
| 4 | UPVC Pipes | Prince/ Astral/ Eq. |
| 5 | UPVC / PP Valves | Prince/ Astral/ Eq. |
| 6 | MS pipes | Jindal/ Tata/ Eq. |
| 7 | Electrical Motor | ABB/Crompton/Kirloskar/Eq. |
| 8 | Blower ( Twin Lobe) | Airvak/ Everest/ Eq. |
| 9 | Filter Press / Centrifuge | VV Eng/ Royal Precession/Eq. |
| 10 | MBBR Media | Pratham/ MR Filter/ Cooldeck/ Eq. |
| 11 | Tube Pack Media | Pratham/ MR Filter/ Cooldeck/Eq. |
| 12 | Diffuser Membrane | SSI/Eq. |
| 13 | DMF & ACF ( in MS) | “GEEC” |
| 14 | DMF & ACF ( in FRP) | Tata/ Pentair/Eq. |
| 15 | Water Meter | Myko/Kranti/Eq. |
| 16 | Rota meter | Pratham/ Filtra/Eq. |
| 17 | Pressure Gauge | Pratham/ Fiebeg/Eq. |
| 18 | Level Sensor | Minlec/GIC/Eq. |
| 19 | pH Sensor & Indicator | Aster/Eq. |
| 20 | Online Monitoring for pH, TSS, BOD & COD | Potence Control/Burket/Eq. |
| 21 | DO meter | Potence Control/Burket/Eq. |
| 22 | Bar Screen | “GEEC” |
| 23 | Micron Cartridge Housing | Pratham/Filtra/Eq. |
| 24 | UF Membrane | Qsep/Eq. |
| 25 | Contractor | Schneider/L&T/Siemens/Eq. |
| 26 | Overload Relay | Schneider/L&T/Siemens/Eq. |
| 27 | MCB | Schneider/L&T/Siemens/Eq. |
| 28 | MPCB | Schneider/L&T/Siemens/Eq. |
| 29 | Ammeter | Meco/Schneider/Eq. |
| 30 | Volt Meter | Meco/Schneider/Eq. |
| 31 | Energy Meter | Meco/Schneider/Eq. |
| 32 | CTS | Reliable/Eq. |
| 33 | SEL SW | Schneider/Teknik/Eq. |
| 34 | Indicating Lamp | Schneider/Teknik/Eq. |
| 35 | PLC with HMI | Delta/Schneider/Mitsubishi/Eq. |
| 36 | VFD | Delta/Schneider/ABB/Eq. |
| 37 | Push button | Schneider/Teknik/Eq. |
| 38 | Timer | GIC/Selec/Eq. |

ANNEXURE VI

SCHEDULE OF EXCLUSION

## Following is excluded from our scope of work

| 1 | All Civil work is excluded from scope of work. |
| --- | --- |
| 2 | Water & Power required for erection & commissioning. |
| 3 | Removal and cleaning of water, debris from the tanks. |
| 4 | All chemicals and consumables. |
| 5 | Approach road to the site. |
| 6 | Conveyance of raw sewage & Treated Sewage to and from the Sewage Treatment Plant. |
| 7 | Plant Lighting, In coming cable, earthing, earth pit & cable tray. |
| 8 | Shed for filters, MCC panel, Blowers & canopy for motors. |
| 9 | Walk way, ladder, puddle pipe & railing for all the tanks are excluded from scope of work. |
| 10 | Loading, Unloading & Shifting of material, MS tanks at site. |
| 11 | Sand Media for Sludge drying beds. |

ANNEXURE VII

COMMERCIAL TERMS & CONDITION

Our price for the above job as given in Annexure IV  will be as below. Rs.  ------------  (Rupees --------------------------- Only)

Above price are exclusive of  Sales tax, 18% GST  packing and forwarding, fright, but inclusive of erection & Commissioning. ( Travelling, Lodging, boarding & food to be provided by for one person during erection & commissioning )

TERMS OF PAYMENT:

#  30 % with work order

#  50 % against proforma invoice prior to dispatch

#  10 % against erection

#  10 % against completion of work

VALIDITY OF PRICE:

The price given in this offer is valid up to 30 days from the date of the submission of offer and will be subject to our confirmation thereafter.

COMPLETION SCHEDULE:

We will complete the entire project within --- to --- weeks.

GURANTEE /WARANTEE:

The treatment plant supplied is guaranteed for period of 12 months from date of commissioning OR 18 months from the date of supply, which ever is earlier. Equipment guarantee is valid against defective workmanship and / or poor performance of the system only. Our liability is limited to repair the same and not subject to any wear/ tear or supply of consumable / spare.

Above guarantee is subject to:

1. Using spare parts/ consumable recommended by us.

2. Operating and Maintenance of the plant as per our Operation.

With thanks and best regards.

Yours faithfully,

For GREENEARTH ENGINEERS & CONSULTANTS.

SATISH RAO